## Summary
RESULT SUMMARY
Air outlet temperature | F | 151.664
LMTD | F | 71.4641
Correction factor | F | 1
Corrected LMTD | F | 71.4641
Finned Area | ft2 | 50428.4951
Face area | ft2 | 470.4151
Air cooler width |  | 15.6805
Tube Details
Tube OD | in | 1
Fin height | in | 0.625
Tube layout |  | Triangular
Tube pitch | in | 2.5
Total tubes | ea | 301.2455
Tubes per row | ea | 75.3114
Power Detail
Air flow rate | acfm | 283641.1251
Pressure drop | inH2O | 0.57902
Break power | bhp | 36.9133
Motor power | bhp | 40.1231

## Calc
PROCESS FLUID DATA |  | 1ST TRIAL | 2ND TRIAL
Name and Phase |  | 48o API hydrocarbon liquid | 48o API hydrocarbon liquid
API degree |  | 48 | 48
SG |  | 0.7883 | 0.7883
Temperature in (T1) | F | 250 | 250
Temperature out (T2) | F | 150 | 150
Average temperature | F | 200 | 200
Heat capacity | Btu/(lb. F) | 0.55 | 0.55 | At average temperature
Dynamic viscosity | cP | 0.51 | 0.51 | At average temperature
Thermal conductivity | Btu/(hr-ft2-F)/ft | 0.0766 | 0.0766
Flow quantity | lb/hr | 273000 | 273000
Heat load | Btu/hr | 15015000 | 15015000
Fouling factor (r dt) | hr-ft2-F/Btu | 0.001 | 0.001
Allowable pressure drop | psi | 5 | 5
AIR DATA
Ambient temperature (t1) | F | 100 | 100
Elevation | ft | sea level | sea level
Altitute correction factor |  | 1 | 1 | see Fig. 10-16 for altitude correction factor
Air heat capacity | Btu/(lb-F) | 0.24 | 0.24
TYPE OF AIR COOLER
Type |  | Forced-draft | Forced-draft
No of fans |  | 2 | 2
Tube OD | in | 1 | 1
Fins | in | 0.625 | 0.625
Tube pitch | in | 2.5 | 2.5
Pitch orientation |  | Triangular | Triangular
No of tube passes (Np) |  | 3 | 3
No of tubes row |  | 4 | 4
Length of tubes | ft | 30 | 30
CALCULATION
Approximate overall transfer area (Ux) | btu/(h-ft2-F) | 4.2 | 4.1664 | see Fig 10-10
Approximate air temperature rise | F | 52 | 51.664
Air outlet temperature (t2) | F | 152 | 151.664
GTTD (Greatest Terminal Temperature Difference) | F | 98 | 98.336
LTTD (Least Terminal Temperature Difference) | F | 50 | 50
LMTD | F | 71.3283 | 71.4641
R correction factor |  | 1.9231 | 1.9356
P correction factor |  | 0.34667 | 0.34443
Correction factor |  | 1 | 1 | see Fig 10-8 or Fig 10-9
C LMTD |  | 71.3283 | 71.4641
Required surface area (Ax) | ft2 | 50120.3436 | 50428.4951
APSF (external area of fin tube) |  | 107.2 | 107.2 | see Fig 10-11
Total face area of bundles (Fa) | ft2 | 467.5405 | 470.4151
Unit width | ft | 15.5847 | 15.6805
APF (total external area/ft of fintube) | ft2/ft | 5.58 | 5.58 | see Fig 10-11
Number of tubes (Nt) |  | 299.4047 | 301.2455
BWG tube |  | 16 | 16
Tube inside cross section area (At) | in2 | 0.5945 | 0.5945 | see Fig 9-25
Thickness | in2 | 0.065 | 0.065 | see Fig 9-25
Tube side mass velocity (Gt) | lb/(ft2-sec) | 184.049 | 182.9243
Modified Reynold Number |  | 313.9659 | 312.0474
Friction factor (f) |  | 0.003 | 0.003 | see Fig 10-12
Correction factor (Y) | psi/ft | 14.5 | 14.5 | see Fig 10-14
Correction factor (B) | psi/tube passes | 0.25 | 0.25 | see Fig 10-14
Correction factor (teta) |  | 0.96 | 0.96 | see Fig 10-19
Pressure drop tube side (ΔPt) | psi | 4.8281 | 4.8281
k (Cp miu/k)^(1/3) |  | 0.12 | 0.12 | see Fig 10-13
J factor |  | 1900 | 1900 | see Fig 10-15
Tube-side film coefficient |  | 251.5862 | 251.5862
Air Quantity (Wa) | lb/hr | 1203125 | 1210949.0555
Air face mass velocity (Ga) | lb/(hr-ft2 face area) | 2573.3064 | 2574.214
Air-side film cofficient (ha) |  | 8.5 | 8.5 | see Fig 10-17
AR (area ratio of fintubee compared to the exterior area of 1 in OD bare tube) | ft2/ft2 | 21.4 | 21.4 | see Fig 10-11
Ax/Ai |  | 24.5977 | 24.5977
1/Ux |  | 0.24002 | 0.24002
Ux |  | 4.1664 | 4.1664
Check |  | -0.033598 | 0
|  | OK | OK
Fan area per fan | ft2 | 93.5081 | 94.083
Fan diameter | ft | 10.9114 | 10.9449
Average air temperature (Ta, avg) | F | 126 | 125.832
Pressure drop factor (Fp) |  | 0.1 | 0.1 | see Fig 10-18 (at average air temperature)
Density ratio (DR) |  | 0.9 | 0.9 | see Fig 10-16 (at average air temperature)
Air static pressure drop | inH2O | 0.44444 | 0.44444
Density ratio (DR) at inlet temperature |  | 0.95 | 0.95 | see Fig 10-16 (at inlet air temperature)
Actual air volume | acfm total | 281808.4932 | 283641.1251
| acfm air per fan | 140904.2466 | 141820.5626
Fan total pressure drop | inH2O | 0.57893 | 0.57902
Fan efficiency |  | 0.7 | 0.7
BHP per fan | BHP per fan | 18.3344 | 18.4566
Speed reducer efficiency |  | 0.92 | 0.92
Actual fan needed | hp per fan | 19.9287 | 20.0616

## Fig 10-14
2
3
4
4
6
7
8
9