## Sheet1
Data
Given | Horizontal Pipe
d | 6 | in | (Inside Diameter)
Q | 200 | gpm
Question
Is the pipe full?
If not, what is liquid height?
What is pipe's equivalent diameter?
Calculation
Q/d2.5 | 2.268
Status | Pipe is Partially Full
x | 0.81892
H/D | 0.68536
H (Liquid Height) | 4.1122 | in
De/D | 1.1869
De (Pipe Equivalent Diameter) | 7.1216 | in