## Calculation
Calculation for Stack Height for Disposing Plant Gases and Vapors
Data
Component |  | Acetylene
Emission rate | lb/min | 100
Molecular weight | lb/lbmol | 26.038
Allowable Concentration of Vapor
Lower explosive limit |  | 2.5%
Allowable downwind concentration | percentage of LEL | 40%
1%
Required Stack Height
Molar flow rate | lbmol/hr | 230.4324
Minimum stack height (see graph) | ft | 25 | for 1-mi/h (1.6 km/h) wind
Distance Downwind of The Stack
Turbulence condition | - | Neutral (moderate turbulence)
Vertical diffusion coefficient (p) | - | 0.05
Distance from the stack for max effluent concentration | ft | 250
Color code:
Input
Input from table/graph
Calculated
Based on wind speed 1 mi/h (1.6 km/h) and p/q = 1
p = vertical diffusion coefficient
q = horizontal diffusion coefficient

## LEL and UEL data
Gas | LEL (%) | UEL (%) | Molecular Weight (g/mol)
Acetaldehyde | 4 | 60 | 44.053
Acetic acid | 4 | 19.9 | 60.052
Acetone | 2.6 | 12.8 | 58.08
Acetyl chloride | 7.3 | 19 | 78.498
Acetylene | 2.5 | 81 | 26.038
Acrolein | 2.8 | 31 | 56.064
Acrylonitrile | 3 | 17 | 53.062
Allyl chloride | 2.9 | 11.1 | 76.525
Ammonia | 15 | 28 | 17.031
Arsine | 5.1 | 78 | 77.945
Benzene | 1.35 | 6.65 | 78.114
1,3-Butadiene | 2 | 12 | 54.092
n-Butane | 1.86 | 8.41 | 58.124
iso-Butane | 1.8 | 8.44 | 58.124
iso-Butene | 1.8 | 9 | 56.108
Butyl acetate | 1 | 8 | 116.159
Butyl alcohol | 1 | 11 | 74.123
Butylene | 1.98 | 9.65 | 56.108
Carbon Disulfide | 1.3 | 50 | 76.143
Carbon Monoxide | 12 | 75 | 28.01
Cyanogen | 6 | 42.6 | 52.036
Cyclobutane | 1.8 | 11.1 | 56.108
Cyclohexane | 1.3 | 8 | 84.162
Cyclohexanol | 1 | 9 | 100.161
Cyclopropane | 2.4 | 10.4 | 42.081
Cyclohexanone | 1 | 9 | 98.145
Decane | 0.8 | 5.4 | 142.286
Diborane | 0.8 | 88 | 27.669
1,1-Dichloroethane | 6 | 11 | 98.959
Diethyl Ether | 1.9 | 36 | 74.123
Diesel fuel | 0.6 | 7.5
Diethanolamine | 2 | 13 | 105.137
Diethylamine | 2 | 13 | 73.139
Dimethyl sulphoxide | 3 | 42 | 78.133
Diisobutyl ketone | 1 | 6 | 128.216
Diisopropyl ether | 1 | 21 | 102.176 | https://axcelgases.com/wp-content/uploads/technical-data/GAS-LEL-and-UEL.pdf
Epichlorohydrin | 4 | 21 | 92.524
Ethane | 3 | 12.4 | 30.07
Ethylene | 2.75 | 28.6 | 28.054
Ethanol | 3.3 | 19 | 46.069
Ethyl acetate | 2 | 12 | 88.106
Ethylamine | 3.5 | 14 | 45.084
Ethylbenzene | 1 | 7.1 | 106.168
Ethyl Chloride | 3.8 | 15.4 | 64.515
Ethylene glycol | 3 | 22 | 62.068
Ethylene oxide | 3 | 100 | 44.053
Fuel Oil No.1 | 0.7 | 5
Furan | 2 | 14 | 68.074
Furfural | 2 | 19 | 96.085
Gasoline | 1.4 | 7.6
Hydrogen sulfide | 4.3 | 46 | 34.082
Isobutane | 1.8 | 9.6 | 58.124
Isobutyl alcohol | 2 | 11 | 74.123
Isophorone | 1 | 4 | 138.209
Isopropanol | 2 | 12 | 60.096
Kerosene Jet A-1 | 0.7 | 5
Methane | 5 | 15 | 16.043
Methyl Acetate | 3 | 16 | 74.079
Methanol | 6.7 | 36 | 32.042
Methyl Chloride | 10.7 | 17.4 | 50.488
Methyl Ethyl Ketone | 1.8 | 10 | 72.107
Mineral spirits | 0.7 | 6.5
Naphthalene | 0.9 | 5.9 | 128.174
n-Heptane | 1 | 6 | 100.205
n-Hexane | 1.25 | 7 | 86.178
n-Pentene | 1.65 | 7.7 | 70.135
Neopentane | 1.38 | 7.22 | 72.151
Neohexane | 1.19 | 7.58 | 86.178
Nitrobenzene | 2 | 9 | 123.111
Nitromethane | 7.3 | 22.2 | 61.04
n-Octane | 1 | 7 | 114.232
iso-Octane | 0.79 | 5.94 | 114.232
n-Pentane | 1.4 | 7.8 | 72.151
iso-Pentane | 1.32 | 9.16 | 72.151
Propane | 2.1 | 10.1 | 44.097
Propyl acetate | 2 | 8 | 102.133
Propylene | 2 | 11.1 | 42.081
Propylene oxide | 2.3 | 36 | 58.08
Pyridine | 2 | 12 | 79.102
Silane | 1.5 | 98 | 32.117
Styrene | 1.1 | 6.1 | 104.152
Tetrahydrofuran | 2 | 12 | 72.106
Toluene | 1.27 | 6.75 | 92.141
Trichloroethylene | 13 | 90 | 131.389
Triptane | 1.08 | 6.69 | 100.205
Turpentine | 0.8
Vinyl acetate | 2.6 | 13.4 | 86.09
Vinyl chloride | 3.6 | 33 | 62.499
p-Xylene | 1 | 6 | 106.168

## Turbulence parameter
Turbulence parameters as given by Bosanquet-Pearson:
| p | q | p/q
Stable (low turbulence) | 0.02 | 0.04 | 0.5
Neutral (moderate turbulence) | 0.05 | 0.08 | 0.625
Very unstable (high turbulence) | 0.1 | 0.16 | 0.625