## Softener Design
Ion Exchange Softener design
Gross flow - Q |  |  |  |  | Resin volume - Vr
| 10 | m3/h | 44.0287 | gpm |  | 813 | L | 28.7109 | ft3
Run length |  |  |  |  | Column internal diameter - D
| 24 | h | 1 | days |  | 914 | mm | 35.9843 | in
Run volume |  |  |  |  | Column cylindrical height - H
| 240 | m3 | 63401.28 | gal |  | 1829 | mm | 72.0079 | in
Feed water Hardness - Ci |  |  |  |  | Resin height - Hr
| 200 | mg/L CaCO3 | 4 | meq/L |  | 1239 | mm | 48.7795 | in
Feed water Sodium concentration |  |  |  |  | Pressure drop at design temperature
| 0 | mg/L | 0 | meq/L |  | 0.37 | bar | 5.3664 | psi
Design temperature |  |  |  |  | Final safety factor from column design [1]
| 20 | deg C | 68 | deg F |  | 1.1
Desired safety factor [1] |  |  |  |  | Contact time
| 1.1 |  |  |  |  | 4.9 | min | 12.3 | BV/h
Regeneration level |  |  |  |  | Hardness leakage - Co
| 150 | g/L_resin |  |  |  | 1 | mg/L CaCO3 | 0.02 | meq/L
NaCl injection concentration - Cr |  |  |  |  | NaCl @ 100% for regeneration
| 10 | % |  |  |  | 122 | kg | 268.9636 | lb
Resin type [2] |  |  |  |  | Diluted NaCl volume for regeneration
AmberLite IRC120 Na | [5 empty] | 1140 | L | 301.1561 | gal
Operating Capacity (OEC): | 1.3 | eq/L |  |  | Water consumption for regeneration
[6 empty] | 7.6 | m3 | 2007.7072 | gal
Overall regeneration duration
[6 empty] | 95 | min | 1.5833 | h
Regeneration step 1 - backwash [3] - Qb
| 7.87 | m3/h | 34.6506 | gpm
| 15 | min | 0.25 | h
Regeneration step 2 - NaCl injection [3] - Qr
| 2.28 | m3/h | 10.0385 | gpm
| 30 | min | 0.5 | h
Regeneration step 3 - displacement [3] - Qd
| 2.28 | m3/h | 10.0385 | gpm
| 35 | min | 0.58333 | h
Regeneration step 4 - fast rinse [3] - Qf
| 13.12 | m3/h | 57.7657 | gpm
| 15 | min | 0.25 | h
RESIN SELECTION RECOMMENDATION & TECHNICAL ADVICE
REKOMENDASI: AmberLite IRC120 Na / TapTec HCR-S sangat ideal untuk aplikasi standar industri & komersial dengan efisiensi biaya optimal.
[1] Safety factor over the calculated resin volume. The final safety factor might be higher because the solver rounds up the resin volume. Typical: 1.05 to 1.15.
[2] Suggested resins: AmberLite IRC120, AmberLite HPR1300, AmberLite HPR1200 or TapTec HCR-S.
[3] Backwash in upflow direction. Operation, injection, displacement and rinse in downflow direction. Displacement is done only with water, no NaCl.

## Resin Database
ION EXCHANGE RESIN DATABASE & SPECIFICATIONS
Resin Name | Manufacturer | Polymer Type | Total Capacity (eq/L) | Bead Size Type | OEC @ 80 g/L (eq/L) | OEC @ 120 g/L (eq/L) | OEC @ 150 g/L (eq/L) | OEC @ 200 g/L (eq/L) | OEC @ 250 g/L (eq/L) | Max Temp (deg C) | pH Range | Application Notes
AmberLite IRC120 Na | DuPont / Dow | Gel Polystyrene (8% DVB) | 2 | Gaussian (0.3 - 1.2 mm) | 0.9 | 1.15 | 1.3 | 1.45 | 1.55 | 120 | 0 - 14 | Standard industrial workhorse SAC resin. Excellent durability and cost-efficiency.
AmberLite HPR1200 Na | DuPont / Dow | Gel Premium UPS (8% DVB) | 2 | Uniform Particle Size (UPS) | 0.95 | 1.2 | 1.35 | 1.5 | 1.6 | 120 | 0 - 14 | High-efficiency UPS SAC resin. Low pressure drop, rapid kinetics, minimal rinse water.
AmberLite HPR1300 Na | DuPont / Dow | High Cross-linked Gel (10% DVB) | 2.2 | Uniform Particle Size (UPS) | 1 | 1.28 | 1.45 | 1.62 | 1.72 | 130 | 0 - 14 | Premium high-capacity UPS SAC resin. Superior resistance to thermal & oxidant stress, high TDS/Hardness.
TapTec HCR-S | DuPont / Dow | Gel Polystyrene (8% DVB) | 2 | Gaussian (0.3 - 1.2 mm) | 0.88 | 1.12 | 1.28 | 1.42 | 1.52 | 120 | 0 - 14 | Potable water certified (NSF/ANSI 61). Ideal for residential, commercial & F&B softening.
Purolite C100E | Purolite | Gel Polystyrene (8% DVB) | 2 | Gaussian (0.3 - 1.2 mm) | 0.88 | 1.13 | 1.28 | 1.43 | 1.53 | 120 | 0 - 14 | Food grade SAC resin widely used in commercial and light industrial applications.
Lewatit S 1567 | Lanxess | Monomodal Gel (8% DVB) | 2 | Monodisperse (UPS) | 0.94 | 1.2 | 1.35 | 1.5 | 1.6 | 120 | 0 - 14 | Monodisperse food-grade SAC resin. High exchange kinetics, high operating capacity.

## Vessel Sizing
STANDARD PRESSURE VESSEL SIZING CATALOG (FRP / STEEL)
Nominal Size (in) | Dia D (in) | Dia D (mm) | Height H (in) | Height H (mm) | Area A (m2) | Area A (ft2) | Min Resin Vol (L) | Max Resin Vol (L) | Nominal Flow @ 20 m/h (m3/h) | Max Peak Flow @ 35 m/h (m3/h)
10x54 | 10 | 254 | 54 | 1372 | 0.0507 | 0.545 | 40 | 55 | 1.01 | 1.77
12x52 | 12 | 305 | 52 | 1321 | 0.0731 | 0.785 | 60 | 80 | 1.46 | 2.56
13x54 | 13 | 330 | 54 | 1372 | 0.0855 | 0.922 | 75 | 100 | 1.71 | 2.99
14x65 | 14 | 356 | 65 | 1651 | 0.0995 | 1.069 | 90 | 125 | 1.99 | 3.48
16x65 | 16 | 406 | 65 | 1651 | 0.1295 | 1.396 | 120 | 160 | 2.59 | 4.53
18x65 | 18 | 457 | 65 | 1651 | 0.164 | 1.767 | 150 | 200 | 3.28 | 5.74
21x62 | 21 | 533 | 62 | 1575 | 0.2231 | 2.405 | 200 | 275 | 4.46 | 7.81
24x72 | 24 | 610 | 72 | 1829 | 0.2922 | 3.142 | 300 | 400 | 5.84 | 10.23
30x72 | 30 | 762 | 72 | 1829 | 0.456 | 4.909 | 450 | 600 | 9.12 | 15.96
36x72 | 36 | 914 | 72 | 1829 | 0.6567 | 7.069 | 650 | 850 | 13.13 | 22.98
42x72 | 42 | 1067 | 72 | 1829 | 0.8941 | 9.621 | 900 | 1200 | 17.88 | 31.29
48x72 | 48 | 1219 | 72 | 1829 | 1.1671 | 12.566 | 1200 | 1500 | 23.34 | 40.85
54x72 | 54 | 1372 | 72 | 1829 | 1.4784 | 15.904 | 1500 | 2000 | 29.57 | 51.74
60x72 | 60 | 1524 | 72 | 1829 | 1.8241 | 19.635 | 1800 | 2400 | 36.48 | 63.84
63x86 | 63 | 1600 | 86 | 2184 | 2.0106 | 21.642 | 2200 | 3000 | 40.21 | 70.37
72x96 | 72 | 1829 | 96 | 2438 | 2.6268 | 28.274 | 3000 | 4200 | 52.54 | 91.94
84x96 | 84 | 2134 | 96 | 2438 | 3.5767 | 38.485 | 4200 | 5800 | 71.53 | 125.18
96x120 | 96 | 2438 | 120 | 3048 | 4.6686 | 50.265 | 6000 | 8000 | 93.37 | 163.4

## Calculation Reference
ION EXCHANGE SOFTENER DESIGN - CALCULATION REFERENCE & FORMULAS
Design Parameter | Formula / Standard Method | Engineering Description & Standard Notes
1. Flow & Volume Conversions | Formula / Rule | Description
Gross Flow (gpm) | Q (m3/h) * 4.40287 | US Gallons per minute conversion
Run Length (days) | Run length (h) / 24 | Days of service cycle
Run Volume (m3) | Q (m3/h) * Run length (h) | Total volume treated per service cycle
Run Volume (gal) | Run Volume (m3) * 264.172 | US Gallons treated per service cycle
2. Water Chemistry Conversions | Formula / Rule | Description
Hardness Ci (meq/L) | Hardness (mg/L CaCO3) / 50 | 1 meq/L = 50 mg/L as CaCO3 = 5 deg fH = 2.8 deg dH = 2.92 gpg
Sodium C_Na (meq/L) | Sodium (mg/L) / 23 | 1 meq/L Na+ = 23 mg/L Na+
Design Temp (deg F) | (Temp_C * 1.8) + 32 | Fahrenheit conversion
3. Resin Operating Capacity & Sizing | Formula / Rule | Description
Operating Capacity OEC (eq/L) | Dynamic Lookup from Resin DB based on Regeneration Level (g/L NaCl) | Net usable capacity per liter of resin under specified regenerant dosage
Total Hardness Load (eq) | Run Volume (m3) * Hardness Ci (meq/L) * 1000 / 1000 | Total chemical equivalents of Ca2+ & Mg2+ to exchange
Resin Volume Vr (L) | (Total Load / OEC) * Safety Factor | Liters of Strong Acid Cation (SAC) resin required
Resin Volume Vr (ft3) | Vr (L) / 28.3168 | Cubic feet of resin
4. Vessel Geometry & Hydraulics | Formula / Rule | Description
Column Diameter D (mm) | Lookup Standard Vessel matching linear velocity 15 - 25 m/h | Internal diameter of cylindrical pressure vessel
Cross-Sectional Area A (m2) | PI() * (D / 1000)^2 / 4 | Vessel internal cross-sectional area
Resin Bed Depth Hr (mm) | (Vr / 1000) / A * 1000 | Height of settled resin bed (Recommended: 800 - 2000 mm)
Column Height H (mm) | Standard shell height (or Hr * 1.75 + bottom distributor) | Straight shell height including 50 - 75% freeboard for backwash
Service Linear Velocity v (m/h) | Q / A | Recommended service rate: 15 - 25 m/h (max 35 m/h peak)
Contact Time EBCT (min) | (Vr / 1000) / Q * 60 | Empty Bed Contact Time (Recommended: 2 - 6 min)
Specific Flow Rate (BV/h) | Q / (Vr / 1000) | Bed Volumes treated per hour (Recommended: 8 - 25 BV/h)
Pressure Drop dP (bar) | 0.015 * v^1.1 * (Hr / 1000) * (1 + 0.025 * (20 - Temp_C)) | Clean bed pressure drop corrected for fluid temperature & viscosity
Final Safety Factor | (Vr_actual * OEC) / Total Load | Effective safety factor provided by actual rounded vessel resin volume
5. Regeneration Chemical & Sequence | Formula / Rule | Description
NaCl @ 100% (kg) | Vr (L) * Regeneration_Level (g/L) / 1000 | Pure dry sodium chloride requirement per regeneration cycle
Diluted NaCl Volume (L) | NaCl_kg / (NaCl_conc% * 1.07) | Volume of 10% brine solution (density ~1.07 kg/L) to inject
Step 1 Backwash Qb (m3/h) | A * 12 * (1 + 0.025 * (Temp_C - 20)) | Upflow velocity 10 - 15 m/h adjusted for temperature, 10 - 15 min duration
Step 2 NaCl Injection Qr (m3/h) | Diluted_Brine_Vol_m3 / (30 / 60) | Downflow brine draw at ~3 BV/h, 30 min duration
Step 3 Displacement Qd (m3/h) | Qr (same slow flow rate as brine draw) | Downflow slow rinse with pure water for 1.5 - 2.0 BV, 30 - 45 min duration
Step 4 Fast Rinse Qf (m3/h) | A * 20 | Downflow service velocity rinse to drain until hardness Co < 1 mg/L, 15 min
Total Regeneration Water (m3) | V_backwash + V_brine_water + V_displacement + V_fast_rinse | Total water consumed for entire regeneration sequence
6. RECOMMENDATION GUIDELINES FOR REGENERATION LEVEL (NaCl Dosing)
Dosing (g/L resin) | OEC (eq/L) & Salt Efficiency | Recommended Application & Target Water Quality
80 - 100 | OEC: 0.88 - 1.05 eq/L ¦ Salt Efficiency > 55% ¦ Leakage: 2.0 - 4.0 mg/L CaCO3 | Ecoâ€‘friendly / lightâ€‘duty residential & small commercial. Lower resin capacity, higher salt usage.
120 - 150 (RECOMMENDED) | OEC: 1.20 - 1.35 eq/L ¦ Salt Efficiency 42 - 48% ¦ Leakage: 0.8 - 1.5 mg/L CaCO3 | Standard industrial & commercial. Best balance between salt cost, resin capacity and water softness.
200 - 250 | OEC: 1.45 - 1.60 eq/L ¦ Salt Efficiency < 32% ¦ Leakage: < 0.5 mg/L CaCO3 | Highâ€‘purity / boiler feed & RO pretreatment. Minimal hardness residuals.
> 250 | OEC > 1.60 eq/L ¦ Very low salt efficiency ¦ Negligible leakage | Rarely used due to excessive salt demand and potential resin stress.
7. RECOMMENDATION GUIDELINES FOR NaCl INJECTION CONCENTRATION (Cr %) | Karakteristik Hidrolika & Kimia | Rekomendasi & Alasan Teknis
Concentration (% w/w) | Hydraulic & Chemical Characteristics | Recommendation & Technical Reasoning
< 6 | Very dilute solution, large injection volume required. | NOT RECOMMENDED: Inefficient use of water and low ion exchange driving force.
8 - 10 (RECOMMENDED) | Ideal viscosity (~1.07 kg/L), optimal Na+ diffusion, safe for resin. | STANDARD INDUSTRY: Provides strong concentration gradient, 30â€‘min injection at ~3 BV/h, uniform distribution.
12-15 | More concentrated, reduced injection volume. | OPTIONAL for large tanks if brine flow can be tightly controlled to avoid channeling.
> 15 (near saturation ~26%) | High viscosity (~1.20 kg/L), risk of channeling and osmotic shock. | NOT RECOMMENDED: Extreme density differences cause uneven flow and potential resin damage.

## Sheet1
Feed flow | 10 | m3/h
Operating hour | 24 | h
Hardness | 200 | mg/L as CaCO3
| 200 | g/m3 as CaCO3
Total daily hardness load | 48000 | g CaCO3
Resin capacity | 1.2 | eq/L
| 60 | g CaCO3/L
Resin volume | 800 | Liters
Recommended linear service velocity | 20 | m3/h/m2 | 15-30
Area | 0.5 | m2
Minimum active resin bed depth | 800 | mm
Selected bed depth | 1000 | mm
Freeboard | 50%
Diameter | 800 | mm |  | 12 | lb NaCl/ft3
Height | 1591.5494 | mm |  | 5.4431 | kg NaCl/ft3
| 2387.3241 |  |  | 192.2216 | kg NaC/m3
Salt mass per cycle | 120 | kg NaCl
Salt dosage | 150 | kg NaCl/m3